## LC-RC
This chart describes the communication protocol between the Line controller and its slaves (Relay controllers). All operations are implemented using ModBus Read Holding Registers and Write Multiple Registers.
1. Ping
Line Controller (Master) sends a ping message to the desired slave (Relay controller) in order to receive pong. Pong consists of current status of the relay controller.
| Message parameters |  | Data part description
| Parameter | Value | bit 15 | bit 14 | bit 13 | bit 12 | bit 11 | bit 10 | bit 9 | bit 8 | bit 7 | bit 6 | bit 5 | bit 4 | bit 3 | bit 2 | bit 1 | bit 0
| Modbus request | 03 (0x03) Read Holding Registers | [15 empty] | RS
| Quantity of Registers | 1 (16 bit)
| Register address start | 0x00
[5 empty] | status reg |  | write reg

## RC register map
The register map of Relay controller is accessed word wise. It means each register is 16 bit wide and by insreasing the address by 1, one is shifting by 16 bit, not 8. Also, the way of accesing the data is not relevant. If one wants to obtain the value of bit Y, of register X, any known modbus command can be used, for example either Read Holding Registers or Read Coils.
Status register (0x00), read only
Register | Address | Access | Description | Bit 15 | Bit 14 | Bit 13 | Bit 12 | Bit 11 | Bit 10 | Bit 9 | Bit 8 | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0 | Bit | Description
Status | 0x00 | R | Status bits reflects the current state of the device. Those registers cannot be written but can be read at any time. | [13 empty] | BB | PS | RS | RS (Relay state) | 0- Off, 1- On.
Setting | 0x01 | W | One can write those bits in order to program the device. Although this register is read-write accessed, its state when read does not reflect the current state, but the value that was written to it. In order to obtain current device state Status register should be read. | [16 empty] | PS (Power source) | 0- Power grid, 1- battery
ID | 0x02 - 0x07 | R | 96 bit (12 byte) unique device ID | [16 empty] | BB (Blackout behaviour) | 0-Relay off, 1- Relay On
String | 0x08 - 0x28 | RW | 64 byte user string. One can use it to create a unique name for the device.
Setting register (0x01), read/ write
|  |  |  | Bit 15 | Bit 14 | Bit 13 | Bit 12 | Bit 11 | Bit 10 | Bit 9 | Bit 8 | Bit 7 | Bit 6 | Bit 5 | Bit 4 | Bit 3 | Bit 2 | Bit 1 | Bit 0 | Bit | Description
[18 empty] | BB | RS | RS (Relay state) | 0- Off, 1- On.
[20 empty] | BB (Blackout behaviour) | 0-Relay off, 1- Relay On